[image: image1.jpg]




Mechanical Ventilation with Heat Recovery (MVHR)
A Mechanical Ventilation System with Heat Recovery (MVHR) shall be installed in accordance with the manufacturer’s instructions. A comprehensive system design incorporating design commissioning data shall be supplied to the installer by the manufacturer detailing the layout and all system components. The installer shall follow the design using the recommended components and shall provide completed installed performance test documentation. All designs and installations shall meet with the requirements of Building Regulations and Best Practice guidance such Domestic Ventilation Compliance Guide 2010 and the NHBC Standard Chapter 3.2.
To be terminated externally using the Titon Q Plus High Flow Brick to ensure performance is not compromised.
To be terminated externally via a Titon roof terminal that meets both the system and roof design and intended for use with continuous mechanical ventilation systems having a maximum airflow resistance of 3Pa.
All switches to be provided by Titon and shall be engraved to show the switch designation such as Boost, SUMMERboost® or Summer Mode and as appropriate to the required operation. Switches should be located in accordance with client instruction and wired in accordance with the chosen unit product handbook and current IET wiring requirements.
Titon HRV2 Q Plus – Consultant Specification

The MVHR unit shall be the Titon HRV2 Q Plus fitted with a Summer Mode facility to allow the supply air fan to be switched off on demand. The unit shall incorporate zero volt boost switching, an adjustable boost timer overrun and include Automatic Frost Protection by means of polynomial speed reduction of the supply fan speed to prolong fresh air supply. The HRV shall be made using light weight EPP giving high levels of thermal insulation surrounded by a sturdy metal enclosure finished in a white powder coat paint measuring 715mm wide x 490mm high (excluding ports) x 415mm deep and weighing max 24kg. The MVHR unit shall be SAP Q qualified and capable of an SFP of 0.56 W/l/s and a heat exchanger efficiency of 90%. The MVHR unit shall also have an EU compliant energy rating label with a minimum rating of A and be CE certified and manufactured under BS EN ISO 9001 and BS EN ISO 14001 and have a 3 year parts & labour guarantee.
894 The Crescent, Colchester Business Park, Colchester, CO4 9YQ

+44 (0) 1206 713801   ventsales@titon.co.uk   www.titon.co.uk

[image: image1.jpg]